## Copeland OPI Master
Compressor Model | Compressor Type | Copeland OPI Valid Key | Refrigerant | Application | Voltage (V) | Phase (Ph) | Frequency (Hz) | Nominal Capacity (BTU/hr) | Input Power (Watts) | Rated Current (Amps) | EER (BTU/Wh) | Mass Flow (lbs/hr) | Displacement (CFM) | Displacement (in³/rev) | Overall Length (in) | Overall Width (in) | Overall Height (in) | Mounting Length (in) | Mounting Width (in) | Mounting Height (in) | Suction Size | Discharge Size | Initial Oil Charge (oz) | Oil Recharge (oz) | Oil Type | Net Weight (lbs) | Internal Free Volume (in³) | LRA High (Amps) | MCC (Amps) | Max Operating Current (Amps) | RLA (MCC / 1.4 Contactor) | RLA (MCC / 1.56 Breaker) | Rated Speed (RPM) | Sound Power (dBA) | Vibration mils(peak-peak) | Copeland Live OPI Link
YAS147K1E-TFE-GBP | Scroll (Two-Stage A2L) | YAS147K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 147000 | 13125 | 16.8 | 11.2 | 2160 | 85.5 | 8.46 | 11.23 | 11.06 | 22.00 | 7.50 | 7.50 | 22.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 142.0 | 410.0 | 125 | 28 | 21.00 | 20.0 | 17.9 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS30K1E-TFE-ASE | Scroll (Two-Stage A2L) | YAS30K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 30000 | 2830 | 3.5 | 10.6 | 441 | 17.6 | 1.74 | 9.70 | 9.70 | 15.86 | 7.50 | 7.50 | 16.50 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 53.0 | 125.0 | 25 | 5.9 | 4.40 | 4.2 | 3.8 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YAS147K1E-TFD-GBP | Scroll (Two-Stage A2L) | YAS147K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 147000 | 13125 | 21.0 | 11.2 | 2160 | 85.5 | 8.46 | 11.23 | 11.06 | 22.00 | 7.50 | 7.50 | 22.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 142.0 | 410.0 | 155 | 35 | 26.20 | 25.0 | 22.4 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS60K1E-TFD-ASC | Scroll (Two-Stage A2L) | YAS60K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 60000 | 5550 | 8.3 | 10.8 | 882 | 35.0 | 3.46 | 9.70 | 9.70 | 17.75 | 7.50 | 7.50 | 18.50 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | RL32-3MAF | 78.0 | 185.0 | 56 | 13.8 | 10.30 | 9.9 | 8.8 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA91K1E-TFD-ERZ | Scroll (Commercial A2L) | YA91K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 91000 | 8270 | 12.6 | 11.0 | 1337 | 52.9 | 5.23 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 91.0 | 280.0 | 95 | 21 | 15.80 | 15.0 | 13.5 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YAS76K1E-TFD-ERZ | Scroll (Two-Stage A2L) | YAS76K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 76000 | 6910 | 10.5 | 11.0 | 1117 | 44.4 | 4.39 | 9.69 | 9.69 | 18.25 | 7.50 | 7.50 | 19.00 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 92.0 | 280.0 | 75 | 17.5 | 13.10 | 12.5 | 11.2 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YA122K1E-TFD-ERZ | Scroll (Commercial A2L) | YA122K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 122000 | 10990 | 16.8 | 11.1 | 1793 | 71.0 | 7.02 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 135.0 | 410.0 | 125 | 28 | 21.00 | 20.0 | 17.9 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YAS91K1E-TFD-ERZ | Scroll (Two-Stage A2L) | YAS91K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 91000 | 8270 | 12.6 | 11.0 | 1337 | 52.9 | 5.23 | 9.69 | 9.69 | 18.50 | 7.50 | 7.50 | 19.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 98.0 | 285.0 | 100 | 21 | 15.80 | 15.0 | 13.5 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YAS91K1E-TF5-ERZ | Scroll (Two-Stage A2L) | YAS91K1E-TF5 | R-454B | Air Conditioning | 200/230 V | 3 | 60 Hz | 91000 | 8270 | 25.2 | 11.0 | 1337 | 52.9 | 5.23 | 9.69 | 9.69 | 18.50 | 7.50 | 7.50 | 19.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 98.0 | 285.0 | 205 | 42 | 31.50 | 30.0 | 26.9 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YA182K1E-TFD-ERT | Scroll (Commercial A2L) | YA182K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 182000 | 16250 | 24.6 | 11.2 | 2675 | 105.8 | 10.46 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | RL32-3MAF | 146.0 | 450.0 | 173 | 39 | 25.40 | 27.9 | 25.0 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS122K1E-TFD-ERZ | Scroll (Two-Stage A2L) | YAS122K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 122000 | 10990 | 17.4 | 11.1 | 1793 | 71.0 | 7.02 | 11.23 | 10.38 | 21.50 | 7.50 | 7.50 | 22.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 140.0 | 415.0 | 130 | 29 | 21.80 | 20.7 | 18.6 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YAS60K1E-TFD-ERZ | Scroll (Two-Stage A2L) | YAS60K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 60000 | 5550 | 8.3 | 10.8 | 882 | 35.0 | 3.46 | 9.70 | 9.70 | 17.75 | 7.50 | 7.50 | 18.50 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | RL32-3MAF | 78.0 | 185.0 | 56 | 13.8 | 10.30 | 9.9 | 8.8 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA61K1E-TFD-ASH | Scroll (Single-Stage A2L) | YA61K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 61000 | 5600 | 8.5 | 10.9 | 895 | 35.6 | 3.52 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | RL32-3MAF | 74.0 | 183.0 | 58 | 14.1 | 10.50 | 10.1 | 9.0 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA29K1E-TFD-ASE | Scroll (Single-Stage A2L) | YA29K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 29000 | 2760 | 4.1 | 10.5 | 426 | 17.0 | 1.68 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 48.0 | 122.7 | 36 | 8.2 | 6.20 | 5.9 | 5.3 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA24K1E-TFD-ASE | Scroll (Single-Stage A2L) | YA24K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 24000 | 2300 | 3.5 | 10.4 | 353 | 14.2 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 47.0 | 122.7 | 32 | 7.3 | 5.50 | 5.2 | 4.7 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YAS174K1E-TFD-GBP | Scroll (Two-Stage A2L) | YAS174K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 174000 | 15535 | 24.5 | 11.2 | 2557 | 101.3 | 10.02 | 11.73 | 11.23 | 22.50 | 7.50 | 7.50 | 23.25 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | RL32-3MAF | 150.0 | 450.0 | 175 | 41 | 30.80 | 29.3 | 26.3 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS174K1E-TFE-GBP | Scroll (Two-Stage A2L) | YAS174K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 174000 | 15535 | 19.6 | 11.2 | 2557 | 101.3 | 10.02 | 11.73 | 11.23 | 22.50 | 7.50 | 7.50 | 23.25 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | RL32-3MAF | 150.0 | 450.0 | 140 | 33 | 24.80 | 23.6 | 21.2 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS91K1E-TFE-ERT | Scroll (Two-Stage A2L) | YAS91K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 91000 | 8270 | 10.1 | 11.0 | 1337 | 52.9 | 5.23 | 9.69 | 9.69 | 18.50 | 7.50 | 7.50 | 19.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 98.0 | 285.0 | 80 | 17 | 12.80 | 12.1 | 10.9 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YA275K1E-TED-GCD | Scroll (Commercial A2L) | YA275K1E-TED | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 275000 | 24550 | 37.2 | 11.2 | 4042 | 159.8 | 15.80 | 14.60 | 11.00 | 27.20 | 7.50 | 7.50 | 28.00 | 2 1/4 Rotalock | 1 3/4 Rotalock | 140 | 130 | RL32-3MAF | 202.0 | 620.0 | 225 | 58 | 43.50 | 41.4 | 37.2 | 3500 | 79 Avg / 84 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS122K1E-TFE-ERZ | Scroll (Two-Stage A2L) | YAS122K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 122000 | 10990 | 13.9 | 11.1 | 1793 | 71.0 | 7.02 | 11.23 | 10.38 | 21.50 | 7.50 | 7.50 | 22.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 140.0 | 415.0 | 105 | 23 | 17.30 | 16.4 | 14.7 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YAS60K1E-TF5-ASC | Scroll (Two-Stage A2L) | YAS60K1E-TF5 | R-454B | Air Conditioning | 200/230 V | 3 | 60 Hz | 60000 | 5550 | 16.6 | 10.8 | 882 | 35.0 | 3.46 | 9.70 | 9.70 | 17.75 | 7.50 | 7.50 | 18.50 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | RL32-3MAF | 78.0 | 185.0 | 120 | 27.5 | 20.60 | 19.6 | 17.6 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA22K1E-TFD-ASA | Scroll (Single-Stage A2L) | YA22K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 22000 | 2120 | 3.2 | 10.4 | 323 | 12.9 | 1.28 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 47.0 | 122.7 | 30 | 6.7 | 5.00 | 4.8 | 4.3 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA49K1E-TFD-ASC | Scroll (Single-Stage A2L) | YA49K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 49000 | 4580 | 6.8 | 10.7 | 720 | 28.5 | 2.82 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | RL32-3MAF | 71.0 | 183.0 | 48 | 11.5 | 8.60 | 8.2 | 7.4 | 3500 | 71 Avg / 76 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YA154K1E-TFD-ERT | Scroll (Commercial A2L) | YA154K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 154000 | 13870 | 21.0 | 11.1 | 2263 | 89.5 | 8.85 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 140.0 | 410.0 | 160 | 36 | 27.00 | 25.7 | 23.1 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max | Open OPI Page
YAS26K1E-TF5-ASE | Scroll (Two-Stage A2L) | YAS26K1E-TF5 | R-454B | Air Conditioning | 200/230 V | 3 | 60 Hz | 26000 | 2480 | 7.7 | 10.5 | 382 | 15.4 | 1.52 | 9.70 | 9.70 | 15.86 | 7.50 | 7.50 | 16.50 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 52.0 | 125.0 | 64 | 14.3 | 10.70 | 10.2 | 9.2 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YAS76K1E-TFE-ERZ | Scroll (Two-Stage A2L) | YAS76K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 76000 | 6910 | 8.4 | 11.0 | 1117 | 44.4 | 4.39 | 9.69 | 9.69 | 18.25 | 7.50 | 7.50 | 19.00 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 92.0 | 280.0 | 60 | 14 | 10.50 | 10.0 | 9.0 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max | Open OPI Page
YA22K1E-TFE-ASA | Scroll (Single-Stage A2L) | YA22K1E-TFE | R-454B | Air Conditioning | 575 V | 3 | 60 Hz | 22000 | 2120 | 2.6 | 10.4 | 323 | 12.9 | 1.28 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 47.0 | 122.7 | 24 | 5.3 | 4.00 | 3.8 | 3.4 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YAS31K1E-TFD-ASE | Scroll (Two-Stage A2L) | YAS31K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 31000 | 2920 | 4.4 | 10.6 | 456 | 18.2 | 1.80 | 9.70 | 9.70 | 15.86 | 7.50 | 7.50 | 16.50 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 53.0 | 125.0 | 38 | 8.6 | 6.50 | 6.1 | 5.5 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
YAS30K1E-TF5-ASE | Scroll (Two-Stage A2L) | YAS30K1E-TF5 | R-454B | Air Conditioning | 200/230 V | 3 | 60 Hz | 30000 | 2830 | 8.6 | 10.6 | 441 | 17.6 | 1.74 | 9.70 | 9.70 | 15.86 | 7.50 | 7.50 | 16.50 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | RL32-3MAF | 53.0 | 125.0 | 70 | 15 | 11.20 | 10.7 | 9.6 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max | Open OPI Page
ZP16K5E-PFV-130 | Scroll (Single-Stage) | ZP16K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 15500 | 1660 | 7.3 | 9.3 | 228 | .92 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 48 | 14 | 9.10 | 10.0 | 9.0 | 3500 | 66 Avg / 71 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP16K5E-PFJ-130 | Scroll (Single-Stage) | ZP16K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 12900 | 1380 | 6.2 | 9.3 | 190 | .92 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 45 | 13 | 8.50 | 9.3 | 8.3 | 2900 | 66 Avg / 71 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP20K5E-PFV-130 | Scroll (Single-Stage) | ZP20K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 20000 | 2040 | 9.1 | 9.8 | 294 | 1.15 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 58 | 15.7 | 10.20 | 11.2 | 10.1 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP21K5E-PFJ-130 | Scroll (Single-Stage) | ZP21K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 17500 | 1750 | 7.9 | 10.0 | 258 | 1.22 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 55 | 15.4 | 10.00 | 11.0 | 9.9 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP21K5E-TF5-130 | Scroll (Single-Stage) | ZP21K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 21000 | 2040 | 6.2 | 10.3 | 309 | 1.22 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 55 | 12 | 7.80 | 8.6 | 7.7 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP21K5E-TFD-130 | Scroll (Single-Stage) | ZP21K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 21000 | 2040 | 3.2 | 10.3 | 309 | 1.22 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 28 | 6.5 | 4.20 | 4.6 | 4.2 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP21K5E-TFE-130 | Scroll (Single-Stage) | ZP21K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 21000 | 2040 | 2.6 | 10.3 | 309 | 1.22 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 20 | 5.0 | 3.30 | 3.6 | 3.2 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP24K5E-PFV-130 | Scroll (Single-Stage) | ZP24K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 24000 | 2330 | 10.4 | 10.3 | 353 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 68 | 18.8 | 12.20 | 13.4 | 12.1 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP24K5E-PFJ-130 | Scroll (Single-Stage) | ZP24K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 19900 | 1930 | 8.7 | 10.3 | 293 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.4 | 122.7 | 65 | 17.5 | 11.40 | 12.5 | 11.2 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP24K5E-TF5-130 | Scroll (Single-Stage) | ZP24K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 24000 | 2300 | 7.0 | 10.4 | 353 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 58 | 13 | 8.50 | 9.3 | 8.3 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP24K5E-TFD-130 | Scroll (Single-Stage) | ZP24K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 24000 | 2300 | 3.5 | 10.4 | 353 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 28 | 6.5 | 4.20 | 4.6 | 4.2 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP24K5E-TFE-130 | Scroll (Single-Stage) | ZP24K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 24000 | 2300 | 2.8 | 10.4 | 353 | 1.40 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 20 | 5.0 | 3.30 | 3.6 | 3.2 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP31K5E-PFV-130 | Scroll (Single-Stage) | ZP31K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 31200 | 2970 | 13.3 | 10.5 | 459 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 50.0 | 122.7 | 79 | 21.4 | 13.90 | 15.3 | 13.7 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP31K5E-PFJ-130 | Scroll (Single-Stage) | ZP31K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 25900 | 2460 | 11.1 | 10.5 | 381 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 50.0 | 122.7 | 75 | 20.3 | 13.20 | 14.5 | 13.0 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP31K5E-TF5-130 | Scroll (Single-Stage) | ZP31K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 31200 | 2940 | 8.9 | 10.6 | 459 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.5 | 122.7 | 73 | 15 | 9.80 | 10.7 | 9.6 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP31K5E-TFD-130 | Scroll (Single-Stage) | ZP31K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 31200 | 2940 | 4.4 | 10.6 | 459 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.5 | 122.7 | 38 | 7.5 | 4.90 | 5.4 | 4.8 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP36K5E-PFV-130 | Scroll (Single-Stage) | ZP36K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 36200 | 3410 | 15.3 | 10.6 | 532 | 2.06 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 112 | 24 | 15.60 | 17.1 | 15.4 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP36K5E-PFJ-130 | Scroll (Single-Stage) | ZP36K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 30000 | 2830 | 12.7 | 10.6 | 441 | 2.06 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 105 | 22.4 | 14.60 | 16.0 | 14.4 | 2900 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP36K5E-TF5-130 | Scroll (Single-Stage) | ZP36K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 36200 | 3380 | 10.3 | 10.7 | 532 | 2.06 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 66.0 | 183.0 | 83 | 17 | 11.10 | 12.1 | 10.9 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP36K5E-TFD-130 | Scroll (Single-Stage) | ZP36K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 36200 | 3380 | 5.1 | 10.7 | 532 | 2.06 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 66.0 | 183.0 | 45 | 8.5 | 5.50 | 6.1 | 5.4 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP36K5E-TFE-130 | Scroll (Single-Stage) | ZP36K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 36200 | 3380 | 4.1 | 10.7 | 532 | 2.06 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 66.0 | 183.0 | 30 | 6.5 | 4.20 | 4.6 | 4.2 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP42K5E-PFV-130 | Scroll (Single-Stage) | ZP42K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 42200 | 3980 | 17.9 | 10.6 | 620 | 2.42 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.0 | 183.0 | 117 | 28 | 18.20 | 20.0 | 17.9 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP42K5E-PFJ-130 | Scroll (Single-Stage) | ZP42K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 35000 | 3300 | 14.8 | 10.6 | 515 | 2.42 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.0 | 183.0 | 110 | 26 | 16.90 | 18.6 | 16.7 | 2900 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP42K5E-TF5-130 | Scroll (Single-Stage) | ZP42K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 42200 | 3940 | 11.6 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 93 | 19 | 12.30 | 13.6 | 12.2 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP42K5E-TFD-130 | Scroll (Single-Stage) | ZP42K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 42200 | 3940 | 5.8 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 46 | 9.5 | 6.20 | 6.8 | 6.1 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP42K5E-TFE-130 | Scroll (Single-Stage) | ZP42K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 42200 | 3940 | 4.6 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 16.90 | 7.50 | 7.50 | 17.65 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 34 | 7.0 | 4.60 | 5.0 | 4.5 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP44K5E-PFV-130 | Scroll (Single-Stage) | ZP44K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 44000 | 4150 | 18.6 | 10.6 | 647 | 2.53 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 74.0 | 183.0 | 117 | 29 | 18.80 | 20.7 | 18.6 | 3500 | 71 Avg / 76 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP44K5E-PFJ-130 | Scroll (Single-Stage) | ZP44K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 36500 | 3440 | 15.4 | 10.6 | 537 | 2.53 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 74.0 | 183.0 | 110 | 27 | 17.50 | 19.3 | 17.3 | 2900 | 71 Avg / 76 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP44K5E-TF5-130 | Scroll (Single-Stage) | ZP44K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 44000 | 4110 | 12.2 | 10.7 | 647 | 2.53 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 93 | 20 | 13.00 | 14.3 | 12.8 | 3500 | 71 Avg / 76 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP44K5E-TFD-130 | Scroll (Single-Stage) | ZP44K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 44000 | 4110 | 6.1 | 10.7 | 647 | 2.53 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 70.0 | 183.0 | 48 | 10 | 6.50 | 7.1 | 6.4 | 3500 | 71 Avg / 76 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP54K5E-PFV-130 | Scroll (Single-Stage) | ZP54K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 54500 | 5090 | 22.8 | 10.7 | 801 | 3.12 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.0 | 183.0 | 134 | 35 | 22.70 | 25.0 | 22.4 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP54K5E-PFJ-130 | Scroll (Single-Stage) | ZP54K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 45200 | 4220 | 18.9 | 10.7 | 665 | 3.12 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.0 | 183.0 | 125 | 33 | 21.40 | 23.6 | 21.2 | 2900 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP54K5E-TF5-130 | Scroll (Single-Stage) | ZP54K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 54500 | 5040 | 15.3 | 10.8 | 801 | 3.12 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 71.0 | 183.0 | 110 | 25 | 16.20 | 17.9 | 16.0 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP54K5E-TFD-130 | Scroll (Single-Stage) | ZP54K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 54500 | 5040 | 7.6 | 10.8 | 801 | 3.12 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 71.0 | 183.0 | 52 | 13 | 8.40 | 9.3 | 8.3 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZP72KCE-TF5-130 | Scroll (Commercial) | ZP72KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 72500 | 6650 | 20.1 | 10.9 | 1065 | 4.15 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 88.0 | 280.0 | 155 | 33 | 21.40 | 23.6 | 21.2 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP72KCE-TFD-130 | Scroll (Commercial) | ZP72KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 72500 | 6650 | 10.0 | 10.9 | 1065 | 4.15 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 88.0 | 280.0 | 75 | 17 | 11.00 | 12.1 | 10.9 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP83KCE-TF5-130 | Scroll (Commercial) | ZP83KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 83500 | 7590 | 23.0 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 195 | 38 | 24.60 | 27.1 | 24.4 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP83KCE-TFD-130 | Scroll (Commercial) | ZP83KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 83500 | 7590 | 11.5 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 95 | 20 | 13.00 | 14.3 | 12.8 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP83KCE-TFE-130 | Scroll (Commercial) | ZP83KCE-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 83500 | 7590 | 9.2 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 80 | 16 | 10.40 | 11.4 | 10.3 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP103KCE-TF5-130 | Scroll (Commercial) | ZP103KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 104000 | 9450 | 28.6 | 11.0 | 1528 | 5.92 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 134.0 | 410.0 | 225 | 47 | 30.50 | 33.6 | 30.1 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP103KCE-TFD-130 | Scroll (Commercial) | ZP103KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 104000 | 9450 | 14.3 | 11.0 | 1528 | 5.92 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 134.0 | 410.0 | 114 | 24 | 15.60 | 17.1 | 15.4 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP103KCE-TFE-130 | Scroll (Commercial) | ZP103KCE-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 104000 | 9450 | 11.4 | 11.0 | 1528 | 5.92 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 134.0 | 410.0 | 90 | 19 | 12.30 | 13.6 | 12.2 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZP137KCE-TF5-250 | Scroll (Commercial) | ZP137KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 137000 | 12340 | 37.4 | 11.1 | 2013 | 7.91 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 300 | 62 | 40.30 | 44.3 | 39.7 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZP137KCE-TFD-425 | Scroll (Commercial) | ZP137KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 137000 | 12340 | 18.7 | 11.1 | 2013 | 7.91 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 150 | 32 | 20.80 | 22.9 | 20.5 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZP182KCE-TE5-425 | Scroll (Commercial) | ZP182KCE-TE5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 182000 | 16250 | 49.2 | 11.2 | 2675 | 10.46 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 146.0 | 450.0 | 340 | 78 | 50.70 | 55.7 | 50.0 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZP182KCE-TED-425 | Scroll (Commercial) | ZP182KCE-TED | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 182000 | 16250 | 24.6 | 11.2 | 2675 | 10.46 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 146.0 | 450.0 | 173 | 39 | 25.40 | 27.9 | 25.0 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
YA67K1E-TFD-ASH | Scroll (A2L R454B) | YA67K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 67000 | 6090 | 9.2 | 11.0 | 960 | 3.86 | 9.69 | 9.69 | 17.75 | 7.50 | 7.50 | 18.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | RL32-3MAF | 88.0 | 280.0 | 75 | 16 | 10.40 | 11.4 | 10.3 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
YA104K1E-TFD-ERZ | Scroll (A2L R454B) | YA104K1E-TFD | R-454B | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 104000 | 9360 | 14.2 | 11.1 | 1490 | 6.00 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | RL32-3MAF | 135.0 | 410.0 | 114 | 24 | 15.60 | 17.1 | 15.4 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD34K5E-PFV-130 | Digital Scroll (Modulating) | ZPD34K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 34500 | 3280 | 14.7 | 10.5 | 507 | 1.95 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 112 | 23 | 15.00 | 16.4 | 14.7 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD34K5E-PFJ-130 | Digital Scroll (Modulating) | ZPD34K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 28600 | 2720 | 12.2 | 10.5 | 421 | 1.95 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 105 | 21 | 13.60 | 15.0 | 13.5 | 2900 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD34K5E-TF5-130 | Digital Scroll (Modulating) | ZPD34K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 34500 | 3250 | 9.8 | 10.6 | 507 | 1.95 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 68.0 | 183.0 | 83 | 16 | 10.40 | 11.4 | 10.3 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD34K5E-TFD-130 | Digital Scroll (Modulating) | ZPD34K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 34500 | 3250 | 4.9 | 10.6 | 507 | 1.95 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 68.0 | 183.0 | 45 | 8.0 | 5.20 | 5.7 | 5.1 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD34K5E-TFE-130 | Digital Scroll (Modulating) | ZPD34K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 34500 | 3250 | 3.9 | 10.6 | 507 | 1.95 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 68.0 | 183.0 | 30 | 6.0 | 3.90 | 4.3 | 3.8 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD42K5E-PFV-130 | Digital Scroll (Modulating) | ZPD42K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 42200 | 3980 | 17.9 | 10.6 | 620 | 2.42 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 77.0 | 183.0 | 117 | 28 | 18.20 | 20.0 | 17.9 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD42K5E-TF5-130 | Digital Scroll (Modulating) | ZPD42K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 42200 | 3940 | 11.6 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 93 | 19 | 12.30 | 13.6 | 12.2 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD42K5E-TFD-130 | Digital Scroll (Modulating) | ZPD42K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 42200 | 3940 | 5.8 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 46 | 9.5 | 6.20 | 6.8 | 6.1 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD42K5E-TFE-130 | Digital Scroll (Modulating) | ZPD42K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 42200 | 3940 | 4.6 | 10.7 | 620 | 2.42 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 34 | 7.0 | 4.60 | 5.0 | 4.5 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD54K5E-PFV-130 | Digital Scroll (Modulating) | ZPD54K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 54500 | 5090 | 22.8 | 10.7 | 801 | 3.12 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 78.0 | 183.0 | 134 | 35 | 22.70 | 25.0 | 22.4 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD54K5E-TF5-130 | Digital Scroll (Modulating) | ZPD54K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 54500 | 5040 | 15.3 | 10.8 | 801 | 3.12 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 73.0 | 183.0 | 110 | 25 | 16.20 | 17.9 | 16.0 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD54K5E-TFD-130 | Digital Scroll (Modulating) | ZPD54K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 54500 | 5040 | 7.6 | 10.8 | 801 | 3.12 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 73.0 | 183.0 | 52 | 13 | 8.40 | 9.3 | 8.3 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD54k5E-TFE-130 | Digital Scroll (Modulating) | ZPD54K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 54500 | 5040 | 6.1 | 10.8 | 801 | 3.12 | 9.70 | 9.70 | 17.65 | 7.50 | 7.50 | 18.40 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 73.0 | 183.0 | 42 | 10 | 6.50 | 7.1 | 6.4 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPD72KCE-TF5-130 | Digital Scroll (Modulating) | ZPD72KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 72500 | 6650 | 20.1 | 10.9 | 1065 | 4.15 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 155 | 33 | 21.40 | 23.6 | 21.2 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD72KCE-TFD-130 | Digital Scroll (Modulating) | ZPD72KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 72500 | 6650 | 10.0 | 10.9 | 1065 | 4.15 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 75 | 17 | 11.00 | 12.1 | 10.9 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD72KCE-TFE-130 | Digital Scroll (Modulating) | ZPD72KCE-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 72500 | 6650 | 8.0 | 10.9 | 1065 | 4.15 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 90.0 | 280.0 | 60 | 13 | 8.40 | 9.3 | 8.3 | 3500 | 74 Avg / 79 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD83KCE-TF5-130 | Digital Scroll (Modulating) | ZPD83KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 83500 | 7590 | 23.0 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 92.0 | 280.0 | 195 | 38 | 24.60 | 27.1 | 24.4 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD83KCE-TFD-130 | Digital Scroll (Modulating) | ZPD83KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 83500 | 7590 | 11.5 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 92.0 | 280.0 | 95 | 20 | 13.00 | 14.3 | 12.8 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD83KCE-TFE-130 | Digital Scroll (Modulating) | ZPD83KCE-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 83500 | 7590 | 9.2 | 11.0 | 1227 | 4.78 | 9.69 | 9.69 | 19.50 | 7.50 | 7.50 | 20.25 | 1 3/4 Rotalock | 1 1/4 Rotalock | 60 | 55 | 3MA | 92.0 | 280.0 | 80 | 16 | 10.40 | 11.4 | 10.3 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD103KCE-TF5-425 | Digital Scroll (Modulating) | ZPD103KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 104000 | 9450 | 28.6 | 11.0 | 1528 | 5.92 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 135.0 | 410.0 | 225 | 47 | 30.50 | 33.6 | 30.1 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD103KCE-TFD-425 | Digital Scroll (Modulating) | ZPD103KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 104000 | 9450 | 14.3 | 11.0 | 1528 | 5.92 | 11.23 | 10.38 | 21.00 | 7.50 | 7.50 | 21.75 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 135.0 | 410.0 | 114 | 24 | 15.60 | 17.1 | 15.4 | 3500 | 75 Avg / 80 Max | 2.5 Avg / 3.5 Max |  | Open OPI Page
ZPD122KCE-TF5-250 | Digital Scroll (Modulating) | ZPD122KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 122000 | 10990 | 33.3 | 11.1 | 1792 | 7.02 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 250 | 54 | 35.10 | 38.6 | 34.6 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD122KCE-TFD-455 | Digital Scroll (Modulating) | ZPD122KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 122000 | 10990 | 16.7 | 11.1 | 1792 | 7.02 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 125 | 28 | 18.20 | 20.0 | 17.9 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD137KCE-TF5-425 | Digital Scroll (Modulating) | ZPD137KCE-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 137000 | 12340 | 37.4 | 11.1 | 2013 | 7.91 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 300 | 62 | 40.30 | 44.3 | 39.7 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD137KCE-TFD-425 | Digital Scroll (Modulating) | ZPD137KCE-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 137000 | 12340 | 18.7 | 11.1 | 2013 | 7.91 | 11.23 | 11.06 | 21.75 | 7.50 | 7.50 | 22.50 | 1 3/4 Rotalock | 1 1/4 Rotalock | 110 | 100 | 3MA | 137.0 | 410.0 | 150 | 32 | 20.80 | 22.9 | 20.5 | 3500 | 76 Avg / 81 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD154KCE-TE5-455 | Digital Scroll (Modulating) | ZPD154KCE-TE5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 154000 | 13750 | 41.7 | 11.2 | 2263 | 8.87 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 144.0 | 450.0 | 320 | 70 | 45.50 | 50.0 | 44.9 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD154KCE-TED-425 | Digital Scroll (Modulating) | ZPD154KCE-TED | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 154000 | 13750 | 20.8 | 11.2 | 2263 | 8.87 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 144.0 | 450.0 | 160 | 35 | 22.70 | 25.0 | 22.4 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD182KCE-TE5-425 | Digital Scroll (Modulating) | ZPD182KCE-TE5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 182000 | 16250 | 49.2 | 11.2 | 2675 | 10.46 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 147.0 | 450.0 | 340 | 78 | 50.70 | 55.7 | 50.0 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPD182KCE-TED-425 | Digital Scroll (Modulating) | ZPD182KCE-TED | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 182000 | 16250 | 24.6 | 11.2 | 2675 | 10.46 | 11.73 | 11.23 | 22.20 | 7.50 | 7.50 | 22.95 | 2 1/4 Rotalock | 1 3/4 Rotalock | 110 | 100 | 3MA | 147.0 | 450.0 | 173 | 39 | 25.40 | 27.9 | 25.0 | 3500 | 77 Avg / 82 Max | 3.0 Avg / 4.0 Max |  | Open OPI Page
ZPS20K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS20K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 20000 | 2040 | 9.1 | 9.8 | 294 | 1.15 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.3 | 122.7 | 58 | 15.7 | 10.20 | 11.2 | 10.1 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS20K5E-PFJ-130 | Two-Stage Scroll (UltraTech) | ZPS20K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 16600 | 1690 | 7.5 | 9.8 | 244 | 1.15 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.3 | 122.7 | 55 | 14.7 | 9.50 | 10.5 | 9.4 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS20K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS20K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 20000 | 2000 | 6.1 | 10.0 | 294 | 1.15 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 55 | 11.5 | 7.50 | 8.2 | 7.4 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS20K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS20K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 20000 | 2000 | 3.0 | 10.0 | 294 | 1.15 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 28 | 5.8 | 3.80 | 4.1 | 3.7 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS26K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS26K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 26000 | 2520 | 11.3 | 10.3 | 382 | 1.50 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.3 | 122.7 | 70 | 20.0 | 13.00 | 14.3 | 12.8 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS26K5E-PFJ-130 | Two-Stage Scroll (UltraTech) | ZPS26K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 21600 | 2090 | 9.4 | 10.3 | 317 | 1.50 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.3 | 122.7 | 65 | 18.5 | 12.00 | 13.2 | 11.9 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS26K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS26K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 26000 | 2480 | 7.5 | 10.5 | 382 | 1.50 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 60 | 14.0 | 9.10 | 10.0 | 9.0 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS26K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS26K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 26000 | 2480 | 3.8 | 10.5 | 382 | 1.50 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 30 | 7.0 | 4.50 | 5.0 | 4.5 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS26K5E-TFE-130 | Two-Stage Scroll (UltraTech) | ZPS26K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 26000 | 2480 | 3.0 | 10.5 | 382 | 1.50 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 47.0 | 122.7 | 24 | 5.6 | 3.60 | 4.0 | 3.6 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS30K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS30K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 30500 | 2900 | 13.0 | 10.5 | 448 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.6 | 122.7 | 79 | 21.4 | 13.90 | 15.3 | 13.7 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS30K5E-PFJ-130 | Two-Stage Scroll (UltraTech) | ZPS30K5E-PFJ | R-410A | Air Conditioning | 220/240 V | 1 | 50 Hz | 25300 | 2410 | 10.8 | 10.5 | 372 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.6 | 122.7 | 75 | 20.3 | 13.20 | 14.5 | 13.0 | 2900 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS30K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS30K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 30500 | 2870 | 8.7 | 10.6 | 448 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.0 | 122.7 | 73 | 15.0 | 9.80 | 10.7 | 9.6 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS30K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS30K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 30500 | 2870 | 4.3 | 10.6 | 448 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.0 | 122.7 | 38 | 7.5 | 4.90 | 5.4 | 4.8 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS30K5E-TFE-XXX | Two-Stage Scroll (UltraTech) | ZPS30K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 30500 | 2870 | 3.5 | 10.6 | 448 | 1.77 | 9.70 | 9.70 | 15.30 | 7.50 | 7.50 | 16.00 | 1 1/4 Rotalock | 1 Rotalock | 25 | 21 | 3MA | 49.0 | 122.7 | 30 | 6.0 | 3.90 | 4.3 | 3.8 | 3500 | 68 Avg / 73 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS35K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS35K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 35500 | 3350 | 15.0 | 10.6 | 522 | 2.06 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.9 | 183.0 | 112 | 24.0 | 15.60 | 17.1 | 15.4 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS35K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS35K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 35500 | 3320 | 10.1 | 10.7 | 522 | 2.06 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 69.0 | 183.0 | 83 | 17.0 | 11.10 | 12.1 | 10.9 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS35K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS35K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 35500 | 3320 | 5.0 | 10.7 | 522 | 2.06 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 69.0 | 183.0 | 45 | 8.5 | 5.50 | 6.1 | 5.4 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS35K5E-TFE-XXX | Two-Stage Scroll (UltraTech) | ZPS35K5E-TFE | R-410A | Air Conditioning | 575 V | 3 | 60 Hz | 35500 | 3320 | 4.0 | 10.7 | 522 | 2.06 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 69.0 | 183.0 | 30 | 6.5 | 4.20 | 4.6 | 4.2 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS40K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS40K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 40000 | 3770 | 16.9 | 10.6 | 588 | 2.30 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.9 | 183.0 | 115 | 26.0 | 16.90 | 18.6 | 16.7 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS40K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS40K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 40000 | 3740 | 11.0 | 10.7 | 588 | 2.30 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 69.0 | 183.0 | 88 | 18.0 | 11.70 | 12.9 | 11.6 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS40K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS40K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 40000 | 3740 | 5.5 | 10.7 | 588 | 2.30 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 69.0 | 183.0 | 46 | 9.0 | 5.80 | 6.4 | 5.8 | 3500 | 70 Avg / 75 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS49K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS49K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 49000 | 4580 | 13.5 | 10.7 | 720 | 2.82 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.5 | 183.0 | 105 | 22.0 | 14.30 | 15.7 | 14.1 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS49K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS49K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 49000 | 4580 | 6.7 | 10.7 | 720 | 2.82 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.5 | 183.0 | 50 | 11.0 | 7.10 | 7.9 | 7.1 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS51K5E-PFV-130 | Two-Stage Scroll (UltraTech) | ZPS51K5E-PFV | R-410A | Air Conditioning | 208/230 V | 1 | 60 Hz | 51500 | 4810 | 21.6 | 10.7 | 757 | 2.96 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 76.5 | 183.0 | 134 | 35.0 | 22.70 | 25.0 | 22.4 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS51K5E-TF5-130 | Two-Stage Scroll (UltraTech) | ZPS51K5E-TF5 | R-410A | Air Conditioning | 200/230 V | 3 | 60 Hz | 51500 | 4770 | 14.1 | 10.8 | 757 | 2.96 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 105 | 23.0 | 14.90 | 16.4 | 14.7 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page
ZPS51K5E-TFD-130 | Two-Stage Scroll (UltraTech) | ZPS51K5E-TFD | R-410A | Air Conditioning | 460/380-420 V | 3 | 50/60 Hz | 51500 | 4770 | 7.0 | 10.8 | 757 | 2.96 | 9.70 | 9.70 | 16.94 | 7.50 | 7.50 | 17.75 | 1 1/4 Rotalock | 1 Rotalock | 42 | 38 | 3MA | 72.0 | 183.0 | 52 | 11.5 | 7.50 | 8.2 | 7.4 | 3500 | 72 Avg / 77 Max | 2.0 Avg / 3.0 Max |  | Open OPI Page